## Slide 1
Monitoring system of Novosibirsk FEL optical channel state using 1-Wire devices
Bykov E.V, Gorbachev Y.I, Serednyakov S.S., Tararyshkin S.V.
BINP SB RAS, Novosibirsk, Russia
Abstract
The Free Electron Laser(FEL) is currently operated at Novosibirsk. Whole facility is based on multi-turn microtron-recuperator and assume operation in three different modes with its own wavelength range of radiation. To ensure the successful conduction of experiments with this radiation, some diagnostic systems, displaying parameters of radiation and state of optical channel, delivering it to user stations are required. The description of recently developed such system, its structure and usage are presented in this article.
1.Novosibirsk FEL Optical channel
2.Main Electrical and mechanical devices used to measure and transfer mirrors and shutters:
Reed switches and 2-contact microswitches – used to represent states of optical objects, by means of changing of state of electric circuit(open or closed)
DS2408 1wire 8-channel addressable switch – used to measure states of optical channel objects and represent them as bits input register values
Raspberry PI – used to run Epics Channel Access server, which read values of DS2408 registers from OWFS server, and represents them as EPICS Process Variables
3.Main software modules, used to transfer measured states
OWFS server – scanning 1Wire bus, reading values of all found devices(DS2408)
OWCas server – reading DS2408 input register values from OWFS server, representing them as values of EPICS Channel Access Process Variables(PVs)
Portable Epics Channel Access server and client modules in main Optical system control application – used to transfer DS2408 values to all computers in FEL control LAN, and user stations
4.Optical Channel state picture on Optical system control application main window
The main purposes of this system are:
Control of state the main optical channel objects (mirrors, shutters)
Inform operators and FEL users, on which FEL stage radiation optical channel is currently switched
Display all track of FEL radiation propagation from its source(undulator) to final point
Inform user if FEL radiation exists on his table or not